## Sheet1
[6 empty] | Date of evaluation: | 2016-09-08
Follow-up evaluation:
[6 empty] | Date Issued to OEMS: | 2016-09-09
IEQ Dashboard
Location: | Cook Wissahickon Elementary School (K-8) |  |  | KEM Project Number: | K1100
Requested by: | Durelle Holmes |  |  | Year Built/Stories: | 1969 | Objective: Evaluate the cafeteria and kindergarten rooms for mold and moisture
ULCS#: | 6410 - 201 E. Salaignac St.
BE: | Bryan Smith
FAC: | Durelle Holmes
Principal: | Michael Lowe
Location (Room/Area) | Findings | Quantity | Category | Corrective Action | Trade | Start Date | End Date
Cafeteria and Stage | Mold growth was observed on tables, walls, fiberglass duct insulation, ceiling tiles, and contents. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/8/16 for the remediation. | Environmental
Cafeteria | Water stained and moldy ceiling tiles were observed. | 2 EA | Mold/Moisture | Replace the impacted ceiling tiles following remediation. | Building Engineer
Cafeteria | The source of moisture impacting the cafeteria and adjacent room appears to be from a malfunctioning AHU. The dehumidifier stationed in the cafeteria failed over the Labor Day weekend leading to the mold growth. This dehumidifier was removed and replaced with 2 units. | N/A | Mold/Moisture | Evaluate and repair the AHU serving the cafeteria. The relative humidity in the cafeteria during the evaluation was 78%. | A/C Refrigeration
Teacher's Storage Room | Mold growth was observed on fiberglass duct insulation and contents. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/8/16 for the remediation. | Environmental
Staff Lunch Room | Mold growth was observed on fiberglass duct insulation . | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/8/16 for the remediation. | Environmental
Operations Storage Room | Mold growth was observed on fiberglass duct insulation. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/8/16 for the remediation. | Environmental
Operations Storage Room | Condensation was dripping from a section of un-insulated chilled water piping. | 6 LF | Mold/Moisture | The chilled water lines should be insulated to prevent condensation. | Building Engineer
Kindergarten Room 1 | Mold growth was observed on cabinetry, chairs, tables and other materials. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/9/16 for the remediation. | Environmental
Kindergarten Room 1 | Chipped and spalling sections of concrete ceiling were observed. | N/A | Safety | The chipped and spalling sections of concrete ceiling should be removed. | Building Engineer
Kindergarten Room 1 | Condensation was dripping from the soffit above the unit ventilator and ceiling tiles were missing. | 1 EA | Mold/Moisture | Evaluate the source of moisture and issue work orders as needed for the repair. The ceiling tiles should be replaced as needed. | Building Engineer
Kindergarten Room 2 | Mold growth was observed on cabinetry, chairs, tables and other materials. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/9/16 for the remediation. | Environmental
Kindergarten Room 2 | Missing ceiling tiles were observed. | 3 EA | Point Source | Replace the missing ceiling tiles. | Building Engineer
Kindergarten Room 2 | A moldy ceiling tile was observed. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Kindergarten Room 2 | A leak was observed on the classroom sink. | 1 EA | Mold/Moisture | Repair or issue work orders for the leaking sink. | Building Engineer
Kindergarten Room 2 Closet | Chilled water was passing through the convector resulting in mold growth and condensation on the floor. | 1 EA | Mold/Moisture | The heating convector should be isolated during the heating season to prevent condensation and mold growth. | Building Engineer
Kindergarten Room 3 | Mold growth was observed on cabinetry, chairs, tables and other materials. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/9/16 for the remediation. | Environmental
Kindergarten Room 3 | This unit ventilator was running without air filters. | 2 EA | Ventilation | The air filters should be installed and the filters throughout the building should be checked and replaced as needed. | Building Engineer
Kindergarten Rooms | The source of moisture leading to the mold growth appeared to be related to the introduction of outdoor air into a conditioned space during construction activity that occurred over the summer. | N/A | Mold/Moisture | The outdoor air intakes grilles should be re-installed. | Capital
Kindergarten Rooms | Missing, damaged, and rotted condensate pans were observed. Condensate was dripping on the components and floor. | N/A | Mold/Moisture | Work orders should be issued for the condensate drip pans as needed. | Building Engineer