## Sheet1
[6 empty] | Date of evaluation: | 2016-09-09
[6 empty] | Follow-up evaluation: | 2016-09-12
[6 empty] | Date Issued to OEMS: | 2016-09-13
IEQ Dashboard
Location: | Cook Wissahickon Elementary School (K-8) |  |  | KEM Project Number: | K1100
Requested by: | Durelle Holmes |  |  | Year Built/Stories: | 1969 | Objective: Evaluate the remaining areas of the building for mold and moisture.
ULCS#: | 6410 - 201 E. Salaignac St.
BE: | Bryan Smith
FAC: | Durelle Holmes
Principal: | Michael Lowe
Location (Room/Area) | Findings | Quantity | Category | Corrective Action | Trade | Start Date | End Date
Room 203 | The return air filter tray was not seated properly. | 1EA | Ventilation | Replace the air filters and adjust the filter tray as needed. | Building Engineer
Room 205 | The return air filter tray was not seated properly. | 1EA | Ventilation | Replace the air filters and adjust the filter tray as needed. | Building Engineer
Room 207 | The return air filter tray was not seated properly. | 1EA | Ventilation | Replace the air filters and adjust the filter tray as needed. | Building Engineer
Room 209 | The unit ventilator was not running. The staff reported is was inoperable. | 1 EA | Ventilation | Evaluate the unit ventilator and restore operation or issue work orders as needed for repair. | Building Engineer
Room 210 | Small delaminated sections of concrete ceiling were observed. | 15 SF | Safety | The delaminated sections of concrete ceiling should be sounded and stabilized as needed. | Building Engineer
Room 211 | A water stained ceiling tile was observed by the closet. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 211 | The occupant reported water leaks into the room during possible from the window or unit ventilator. | N/A | Mold/Moisture | The source of water intrusion should be evaluated and work orders issued as needed for the repair. | Building Engineer
Room 103 | A missing ceiling tile was observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 105 | A missing ceiling tile was observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 106 | A missing ceiling tile was observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 106 | The occupant reported water leaks into the room during possible from the window or unit ventilator. | N/A | Mold/Moisture | The source of water intrusion should be evaluated and work orders issued as needed for the repair. | Building Engineer
Room 108 | A water stained ceiling tile was observed. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 109 | A ceiling tile was missing. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 105 | A water stained ceiling tile was observed. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 110 | A missing ceiling tile was observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Hallway outside Room 10 | A water stained ceiling tile was observed. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 111 | Water stained ceiling tiles were observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 111 | The return air filter tray was not seated properly. | 1EA | Ventilation | Replace the air filters and adjust the filter tray as needed. | Building Engineer
Basement Hallway | Water stained and moldy ceiling tiles were observed. | 12 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer | 2016-09-09 | 2016-09-11
Art Room 6 | Mold growth was observed on the wooden cabinetry, metal cabinetry, chairs, tables, doors and door frames. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/12/16 for the remediation. | Environmental | 2016-09-09 | 2016-09-11
Art Room 6 | A missing ceiling tiles were observed and condensation appeared to be leaking from the suspended ceiling. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer | 2016-09-09 | 2016-09-11
Art Room 6 | Particulate accumulation was observed on the supply diffusers and ceiling tiles. | All | Point Source | The supply diffusers and ceiling tiles should be cleaned and/or replaced as needed. | Building Engineer | 2016-09-09 | 2016-09-11
Art Room 6 | Delaminated 9"x9" floor tile was observed. | 125 SF | Point Source | An asbestos DDC should be issued for the repair of the floor tile. | OEMS
Music Room 5 | Particulate accumulation was observed on the supply diffusers and ceiling tiles. | All | Point Source | The supply diffusers and ceiling tiles should be cleaned and/or replaced as needed. | Building Engineer | 2016-09-09 | 2016-09-11
Art Room 6 | Limited mold growth was observed on the wooden cabinetry. | N/A | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/12/16 for the remediation. | Environmental | 2016-09-09 | 2016-09-11
Art Room 6 and Instrumental Room | The air handler located in the gym closet was running, however, there was no air distribution to this room. Condensate was leaking from the air handler and standing water observed on the floor. | N/A | Ventilation | Evaluate the air handler, repair condensate leaks and restore air distribution to the music suite. | Building Engineer
Music Suite Air Handler Room | Delaminated 9"x9" floor tile was observed from condensation leaking on the floor. | 150 SF | Point Source | An asbestos DDC should be issued for the repair of the floor tile. | OEMS
Instrumental Room | Particulate accumulation was observed on the supply diffusers and ceiling tiles. | All | Point Source | The supply diffusers and ceiling tiles should be cleaned and/or replaced as needed. | Building Engineer
Instrumental Room | Water stained ceiling tiles were observed. | 5 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Practice Room A | A missing ceiling tile was noted. | 1 EA | Point Source | Replace the missing ceiling tile. | Building Engineer
Practice Room A | Particulate accumulation was observed on the supply diffusers and ceiling tiles. | All | Point Source | The supply diffusers and ceiling tiles should be cleaned and/or replaced as needed. | Building Engineer
Room 3 | The unit ventilator cabinet was rusted out exposing the outdoor air to a conditioned space. | 1 EA | Mold/Moisture | The unit ventilator cabinet should be repaired or replaced. | TBD
Room 3 Closet | Mold growth was observed on the fiberglass pipe insulation. | 30 LF | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/12/16 for the remediation. | Environmental | 2016-09-12 | 2016-09-12
Music Office | Mold growth was observed on a small section of the metal desk. | <1SF | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/12/16 for the remediation. | Environmental | 2016-09-12 | 2016-09-12
Gym Boy's Room | A missing ceiling tile was observed and condensation appeared to be leaking from a pipe. | 1 EA | Mold/Moisture | Evaluate above the suspended ceiling for the source of moisture and issue work orders as needed for the repair. The ceiling tile should be replaced as needed. | Building Engineer
Room 1 Closet | This closet was not accessible, the C.A. was not able to open. | 1 EA | N/A | This closet should be opened for evaluation. | OEMS