## Sheet1
[6 empty] | Date of evaluation: | 2016-09-19
Follow-up evaluation:
[6 empty] | Date Issued to OEMS: | 2016-09-21
IEQ Dashboard
Location: | Lincoln High School |  |  | KEM Project Number: | K1100
Requested by: | Francine Locke |  |  | Year Built: | 2009 | Objective: Evaluate the IMC and Room 102 for mold and moisture
ULCS#: | 8010
BE: | Dave
FAC: | Keith Guess
Principal:
Location (Room/Area) | Findings | Quantity | Category | Corrective Action | Trade | Start Date | End Date
Room 102 | Mold growth was observed on the wallboard to the right of the unit ventilator. | 1 SF | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/20/16 for the remediation. | Environmental
Room 102 | The 12"x12" floor tile located in from of the unit ventilator was missing and damaged. | 80 SF | Point Source | Replace the damaged section of floor tile. | Carpentry
Room 102 | The source of moisture impacting the wallboard and floor tile was reported as a leaking unit ventilator. The unit ventilator was not running at the time of the evaluation. | 1 EA | Mold/Moisture | The unit ventilator should be evaluate and repaired or work orders issued as needed. | Building Engineer
Room 102 | Water stained ceiling tiles were observed above the unit ventilator. | 7 EA | Mold/Moisture | An evaluation should be conducted above the suspended ceiling for the source of moisture and work orders issued as needed for repair. The ceiling tiles should be replaced. | Building Engineer
Hallway outside Room 106 | Condensate was leaking from an insulated duct located above the suspended ceiling. | 6 LF | Mold/Moisture | The impacted insulation should be removed and replaced. | A/C Refrigeration
Hallway outside Room 106 | Water stained and missing ceiling tiles were observed from the water intrusion. | 8 EA | Mold/Moisture | The missing and water ceiling tiles should be replaced. | Building Engineer
IMC | Approximately 90 SF of mold growth was distributed over 180 LF of the exposed HVAC supply branches. | 90 SF | Mold/Moisture | A mold Design Data Collection (DDC) package was issued on 9/20/16 for the remediation. | Environmental
IMC | The source of moisture impacting the duct work was not determined. | N/A | Mold/Moisture | Evaluate the A/C system and adjust or repair as needed to prevent condensation and mold growth. | A/C Refrigeration
IMC Hall to 149 | Ceiling tiles were painted to hide staining or moldy growth. This was reported as a concern by the occupants. No signs of active leaks were observed at this location. | 5 EA | Mold/Moisture | Replace the ceiling tiles that were painted to hide staining. | Building Engineer
IMC Office 136 | Water stained and moldy ceiling tiles were observed. | 4 EA | Mold/Moisture | An evaluation should be conducted above the suspended ceiling for the source of moisture and work orders issued as needed for repair. The ceiling tiles should be replaced. | Building Engineer
IMC | The B.E. did not have access to several rooms within the IMC including 137, 137A, 136A, 138, 133 B. | 5 EA | N/A | A key for this rooms should be provided to the Building Engineer. These rooms should also be checked for issues relative to mold and moisture. | Locksmith
IMC MDF 134 | A leak was observed on the condensate pump associated with the A/C unit. | 1 EA | Mold/Moisture | Evaluate and repair or replace the leaking condensate pump. | A/C Refrigeration
IMC MDF 134 | Delaminated 12"x12" floor tile was observed in front of the A/C unit. | 60 SF | Point Source | The impacted 12"x12" floor tile should be removed. | Carpentry