## Sheet1
[6 empty] | Date of evaluation: | 2016-12-13
Follow-up evaluation:
[6 empty] | Date Issued to OEMS: | 2016-12-13
IEQ Dashboard
Location: | Bethune Elementary School (K-8) |  |  | KEM Project Number: | K1100
Requested by: | Francine Locke |  |  | Year Built/Stories: | 1970/3 | Objective: Perform IEQ Evaluation as requested by PFT
ULCS#: | 7510 - 3301 Old York Road
BE: | Cary Middleton (cdmiddleton)
FAC: | Derek Parker (deparker)
Nurse: | Karen Giammanco (kagiammanco)
Principal: | Jamina Dingle (jclay)
Location (Room/Area) | Findings | Quantity | Category | Corrective Action | Trade | Start Date | End Date
Room 102 | The heat is not working in this room due to an inoperable unit ventilator motor. The classroom was relocated to another room 4 weeks ago. | 1 EA | Ventilation | Repair the unit ventilator and restore heat to this room. | Steamfitting
1st Floor Hallway outside the Community Room | A leaking hot water line was observed above the suspended ceiling. The fiberglass pipe insulation was removed from the impacted section of this line and the ceiling tiles were removed. A slow drip was noted. | 1 EA | Mold/Moisture | Repair the leaking hot water line in the first floor hallway. | Steamfitting
Room 113 | This room was reported as being under heated. The B.E. indicated the heat is working, however, sections of the heating coil are clogged and restricting the flow of hot water. | 1 EA | Ventilation | Evaluate and repair the unit ventilator as needed to provide adequate heat. | Steamfitting